| Product Drawing | Unit Tag: |  |  | 13600 Industrial Park Blvd. Minneapolis, MN 55441. www.DaikinApplied.com; Software Version:. |
| --- | --- | --- | --- | --- |
| Product: Centrifugal Chiller Starter | Project Name: |  |  |  |  |  |
| Model: D3WD | Sales Office: |  |  |  |  |  |
| Sales Engineer: | Date: | Ver/Rev: | Sheet 1 of 1 | Scale: NTS | Tolerance: +/-1.0” | Dwg Units: in [mm] |
| No change to this drawing may be made unless approved in writing by Daikin Applied. Purchaser must determine that the equipment is fit and sufficient for the job specifications. |  |  |  |  |  |  |

00

00

D3WD11-D3WD43 Wye Delta Free Standing Starters

NOTE: For starters equipped with optional power factor correction capacitors and/or fused disconnect switches, use Drawing D3WD11-65, which is 78 inches high rather than this 66-inch high unit.

NOTES:

- All dimensions are in inches (mm).

- Free-standing Models RSVT have optional 18-inch legs as shown in front view.

- Power factor correction capacitors cannot be mounted in this size enclosure.

- Weight of free-standing model is 450 lbs (204 kg).

- The breaker sizes shown are for the breaker installed in the starter and used as a unit disconnect switch. Use the MOCP shown in the unit’s Technical Data Sheet to size any upstream protection devices required by local code.

D3WD11-D3WD43 Wye Delta Free Standing Starters

NOTE: For starters equipped with optional power factor correction capacitors and/or fused disconnect switches, use Drawing D3WD11-65, which is 78 inches high rather than this 66-inch high unit.

NOTES:

- All dimensions are in inches (mm).

- Free-standing Models RSVT have optional 18-inch legs as shown in front view.

- Power factor correction capacitors cannot be mounted in this size enclosure.

- Weight of free-standing model is 450 lbs (204 kg).

- The breaker sizes shown are for the breaker installed in the starter and used as a unit disconnect switch. Use the MOCP shown in the unit’s Technical Data Sheet to size any upstream protection devices required by local code.

| Electrical Data |  |  |
| --- | --- | --- |
| Starter Model | Incoming Lug Size, Power Block | Outgoing Connection Hole Size |
| D3WD11 | (2) #6 - 300 | 0.45 in |
| D3WD12 | (2) #6 - 300 | 0.45 in |
| D3WD14 | (2) #6 - 300 | 0.45 in |
| D3WD15 | (2) #6 - 300 | 0.45 in |
| D3WD25 | (2) #6 - 300 | 0.45 in |
| D3WD31 | (2) #6 - 300 | 0.45 in |
| D3WD34 | (2) #6 - 300 | 0.45 in |
| D3WD43 | (2) #6 - 350 | 0.45 in |

| Electrical Data |  |  |  |
| --- | --- | --- | --- |
| Starter Model | Breaker Size | Incoming Lug Size |  |
|  |  | Circuit Breaker | Disconnect Switch |
| D3DW11 | 200A | #6-350 | #6-350 |
| D3DW12 | 250A | #6-350 | #6-350 |
| D3DW14 | 250A | #6-350 | #6-350 |
| D3DW15 | 300A | (2) #3/0-500 | #6-350 |
| D3DW25 | 400A | (2) #3/0-500 | (2) #3/0-500 |
| D3DW31 | 400A | (2) #3/0-500 | (2) #3/0-500 |
| D3DW34 | 500A | (2) #3/0-500 | (2) #3/0-500 |
| D3DW43 | 600A | (2) #3/0-500 | (2) #3/0-500 |